## Data
Technical information to the unit certificate
|  |  | Version number of the template | 2 | Version date of the template | 2023-09-27
ID | Attributreihenfolge | Attributnummer | Category | Attribute name | Explanation of data input | Data source | Formula symbol | Unit | Data type | Value1 | Value2 | Value3 | Value4 | Value5 | PGU 1 | PGU 2 | PGU 3 | PGU 4 | PGU 5 | PGU 6 | PGU 7 | PGU 8 | PGU 9 | PGU 10 | PGU 11 | PGU 12 | PGU 13 | PGU 14 | PGU 15 | PGU 16 | PGU 17 | PGU 18 | PGU 19 | PGU 20 | PGU 21 | PGU 22 | PGU 23 | PGU 24 | PGU 25 | PGU 26 | PGU 27 | PGU 28 | PGU 29 | PGU 30 | PGU 31 | PGU 32 | PGU 33 | PGU 34 | PGU 35 | PGU 36 | PGU 37 | PGU 38 | PGU 39 | PGU 40 | PGU 41 | PGU 42 | PGU 43 | PGU 44 | PGU 45 | PGU 46 | PGU 47 | PGU 48 | PGU 49 | PGU 50 | PGU 51 | PGU 52 | PGU 53 | PGU 54 | PGU 55 | PGU 56 | PGU 57 | PGU 58 | PGU 59 | PGU 60 | PGU 61 | PGU 62 | PGU 63 | PGU 64 | PGU 65 | PGU 66 | PGU 67 | PGU 68 | PGU 69 | PGU 70 | PGU 71 | PGU 72 | PGU 73 | PGU 74 | PGU 75 | PGU 76 | PGU 77 | PGU 78 | PGU 79 | PGU 80 | PGU 81 | PGU 82 | PGU 83 | PGU 84 | PGU 85 | PGU 86 | PGU 87 | PGU 88 | PGU 89 | PGU 90 | PGU 91 | PGU 92 | PGU 93 | PGU 94 | PGU 95 | PGU 96 | PGU 97 | PGU 98 | PGU 99 | PGU 100
A01.001 | 1 | 1 | 01 Certification | Manufacturer of the entire generating unit | Manufacturer e.g. of the PV, wind turbine or combustion engine (CE) generation unit | Manufacturer | - | - | text
A01.002 | 2 | 2 | 01 Certification | Type designation of the entire generating unit | Complete unique type designation according to unit certificate | Manufacturer or unit certifier | - | - | text
A01.003 | 3 | 3 | 01 Certification | Certification body | Company name of the certification body | Unit certifier | - | - | text
A01.004 | 4 | 4 | 01 Certification | Certificate number | Revision level must be indicated (e.g.: 101-1). | Unit certifier | - | - | text
A01.005 | 5 | 5 | 01 Certification | Date of issue of the first version of the certificate | DD.MM.YYYY | Unit certifier | - | - | date
A01.006 | 6 | 6 | 01 Certification | Issue date of the version of the certificate used here | DD.MM.YYYY | Unit certifier | - | - | date
A01.007 | 7 | 7 | 01 Certification | Expiry date of the validity of the certificate | DD.MM.YYYY | Unit certifier | - | - | date
A01.008 | 8 | 8 | 01 Certification | Sequence number according to unit certificate | To be indicated where applicable | Unit certifier | - | - | text
A01.009 | 9 | 9 | 01 Certification | Complies with VDE-AR-N 4110? (issue date if applicable) | Select the used issue date, if applicable. | Unit certifier | - | - | text | Value1: No; Value2: 2018; Value3: 2023
A01.010 | 10 | 10 | 01 Certification | Complies with VDE-AR-N 4120? (issue date if applicable) | Select the used issue date, if applicable. | Unit certifier | - | - | text | Value1: No; Value2: 2015; Value3: 2018
A01.011 | 11 | 11 | 01 Certification | Complies with VDE-AR-N 4130? (issue date if applicable) | Select the used issue date, if applicable. | Unit certifier | - | - | text | Value1: No; Value2: 2018
A01.012 | 12 | 12 | 01 Certification | Conditions and restrictions of the unit certificate | Additional notes on constraints and limitations of the electrical properties and characteristics to be observed if not already covered by other attributes (also to be found on the cover sheet of the unit certificate) | Unit certifier | - | - | text
A01.013 | 1 | 13 | 02 Generation unit | Generation unit type | 1 or 2 | Unit certifier | - | - | integer | Value1: 1; Value2: 2
A01.014 | 2 | 14 | 02 Generation unit | Permitted relevant software / firmware versions | If applicable, list software / firmware versions line by line that are relevant for the fulfilment of the electrical properties of the generating unit. Use the following notation: Generation unit: <version> Inverter control: <version> Pitch control: <version> Operation control: <version> Power control: <version> Voltage regulator: <version> Protection device: <version> ... | Unit certifier | - | - | text
A01.015 | 3 | 15 | 02 Generation unit | Rated voltage | Voltage for which the components of the generating unit are rated (e.g. 230 V, 400 V, 690 V). | Unit certifier | UrE | V | decimal number
A01.016 | 4 | 16 | 02 Generation unit | Rated current | According to FGW TR 3, reference current for the harmonic, interharmonic and supraharmonic harmonics, usually corresponds to the rated current Ir | Unit certifier | In | A | decimal number
A01.017 | 5 | 17 | 02 Generation unit | Nominal frequency | Mains frequency for which the generating plant is designed (50 Hz or 60 Hz) | Unit certifier | fn | Hz | decimal number
A01.018 | 6 | 18 | 02 Generation unit | Rated effective power | Active power of the generating unit at nominal conditions specified by the manufacturer | Unit certifier | PrE | kW | decimal number
A01.019 | 7 | 19 | 02 Generation unit | Max. Active power | Highest 10-minute average value of active power, also corresponds to P600 | Unit certifier | PEmax | kW | decimal number
A01.020 | 8 | 20 | 02 Generation unit | If applicable, explain the dependencies of the max. active power output from the ambient conditions. | E.g. dependencies on ambient temperature / air pressure | Manufacturer | - | - | text
A01.021 | 9 | 21 | 02 Generation unit | Technical minimum effective power | For type 1, in special cases also for type 2 | Unit certifier | PEmin | kW | decimal number
A01.022 | 10 | 22 | 02 Generation unit | Rated apparent power | Apparent power for which the components of the generating unit are rated | Unit certifier | SrE | kVA | decimal number
A01.023 | 11 | 23 | 02 Generation unit | Max. Apparent power | Maximum 10-minute average apparent power, if not measured, the max. apparent power shall be determined from the P(Q) diagrams of the entire generating unit. | Unit certifier | SEmax | kVA | decimal number
A01.024 | 12 | 24 | 02 Generation unit | Active power reduction in favour of the reactive power requirement possible? | Yes indicate if the generating unit can reduce the active power in favour of the reactive power, this may be necessary to comply with the grid operator's requirements in case of insufficient reactive power capacity. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.025 | 13 | 25 | 02 Generation unit | Stationary reactive power compensation possible (if P = 0)? | Yes, if the generating unit can feed in reactive power independently of the active power generation, e.g. when there is no wind or no solar radiation. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.026 | 14 | 26 | 02 Generation unit | Min. adjustable active power gradient in normal operation with setpoint selection | Min. adjustable active power gradient in normal operation with setpoint selection referred to PrE (see ID A01.018) per second | Manufacturer |  | % PrE/s | decimal number
A01.027 | 15 | 27 | 02 Generation unit | Max. adjustable active power gradient in normal operation with setpoint selection | Max. adjustable active power gradient in normal operation with setpoint selection referred to PrE (see ID A01.018) per second | Manufacturer |  | % PrE/s | decimal number
A01.028 | 16 | 28 | 02 Generation unit | Active power specification with a resolution of 1 % or smaller possible? (optional specification) | Valid over the total range from technical minimum active power PEmin (see A01.021) to max. active power PEmax (see ID A01.019). | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.029 | 17 | 29 | 02 Generation unit | Min. Switch-on voltage | Min. setting value according to VDE-AR-N 4110/20/30 chapter 10.4.1 | Manufacturer |  | V | decimal number
A01.030 | 18 | 30 | 02 Generation unit | Max. Switch-on voltage | Max. Setting value according to VDE-AR-N 4110/20/30 chapter 10.4.1 | Manufacturer |  | V | decimal number
A01.031 | 19 | 31 | 02 Generation unit | Min. Switch-on frequency | Min. setting value according to VDE-AR-N 4110/20/30 chapter 10.4.1 | Manufacturer |  | Hz | decimal number
A01.032 | 20 | 32 | 02 Generation unit | Max. Switch-on frequency | Max. Setting value according to VDE-AR-N 4110/20/30 chapter 10.4.1 | Manufacturer |  | Hz | decimal number
A01.033 | 21 | 33 | 02 Generation unit | Are the switch-on waves parameterizable in undisturbed network operation? | Vgl. VDE-AR-N 4110/20/30 Chapter 10.4.1 | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.047 | 1 | 47 | 02 Generation unit | Min. voltage for continuous operation | Specify the minimum voltage at which the generating plant can remain permanently connected to the grid (based on Figure 4 in VDE-AR N 4110). | Manufacturer |  | V | decimal number
A01.048 | 2 | 48 | 02 Generation unit | Max. voltage for continuous operation | Specify the maximum voltage at which the generating plant can remain permanently connected to the grid (based on Figure 4 in VDE-AR N 4110). | Manufacturer |  | V | decimal number
A01.049 | 3 | 49 | 02 Generation unit | Min. frequency for continuous operation | Specify the minimum frequency at which the generating plant can remain permanently connected to the grid (based on Figure 4 in VDE-AR N 4110). | Manufacturer |  | Hz | decimal number
A01.050 | 4 | 50 | 02 Generation unit | Max. frequency for continuous operation | Specify the maximum frequency at which the generating plant can remain permanently connected to the grid (based on Figure 4 in VDE-AR N 4110). | Manufacturer |  | Hz | decimal number
A01.034 | 1 | 34 | 03 Components | Manufacturer/type of relevant components | If applicable, list the manufacturer/type (including clear assignment to e.g. power/voltage) of all components line by line that are relevant for the fulfilment of the electrical characteristics of the generating unit. Use the following notation: Generator: <manufacturer/type> Excitation system: <manufacturer/type> Regulator: <manufacturer/type> Engine: <manufacturer/type> Protection device: <manufacturer/type> Switchgear: <manufacturer/type> Inverter: <manufacturer/type> Transformer: <manufacturer/type> ... | Manufacturer or unit certifier | - | - | text
A01.035 | 2 | 35 | 03 Components | Reference of the rated apparent power of the generator | According to DIN EN 60909-0:2016 for calculation of the continuous short-circuit current (Fig. 15/16) | Manufacturer | SrG | kVA | decimal number
A01.036 | 3 | 36 | 03 Components | Generator type (only for type 1) | According to DIN EN 60909-0:2016 for calculation of the continuous short-circuit current (Fig. 15/16) | Manufacturer | - | - | text | Value1: turbo generator; Value2: salient-pole generator
A01.037 | 4 | 37 | 03 Components | Generator series (only for type 1) | According to DIN EN 60909-0:2016 for calculation of the continuous short-circuit current (Fig. 15/16) | Manufacturer | - | - | integer | Value1: 1; Value2: 2
A01.038 | 5 | 38 | 03 Components | Rated apparent power of the power converter (only for type 2) | For the assessment chapter 11.2.2.4 of VDE-AR-N 4110/20/30 | Manufacturer | Sr Str | kVA | decimal number
A01.039 | 6 | 39 | 03 Components | Line-commutated converters with DC intermediate circuit exists? (only for type 2) | For the assessment chapter 11.2.2.4 of VDE-AR-N 4110/20/30 | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.040 | 7 | 40 | 03 Components | Pulse number of the power converter (only for type 2) | For the assessment chapter 11.2.2.4 of VDE-AR-N 4110/20/30 | Manufacturer | p | - | integer
A01.041 | 8 | 41 | 03 Components | Most unfavourable control angle of the current converter (only for type 2) | For the assessment chapter 11.2.2.4 of VDE-AR-N 4110/20/30 | Manufacturer | α | ° | decimal number
A01.042 | 9 | 42 | 03 Components | Modulation type used in inverter (only for type 2) | For the evaluation scheme of network effects, see Annex B.9.8 (VDE-AR-N 4110), B.9.4 (VDE-AR-N 4120) or B.6.5 (VDE-AR-N 4130). | Manufacturer | - | - | text | Value1: line-commutated; Value2: Pulse modulated < 1 kHz; Value3: Pulse modulated ≥ 1 kHz
A01.043 | 1 | 43 | 04 Simulation | Simulation software | Simulation software to be used for the model of the generating unit (usually PowerFactory or Matlab). | Manufacturer | - | - | text | Value1: DIgSILENT PowerFactory; Value2: Mathworks MATLAB / Simulink
A01.044 | 2 | 44 | 04 Simulation | Simulationssoftwareversion | Version of the simulation software version in which the model of the generating unit was created. | Manufacturer | - | - | text
A01.045 | 3 | 45 | 04 Simulation | Validated unit model | Exact file name | Manufacturer or unit certifier | - | - | text
A01.046 | 4 | 46 | 04 Simulation | Checksum of the validated unit model | MD5 or SHA-256 checksum of the validated unit model or container file, which is required for the verification by the PGS certifier | Manufacturer or unit certifier | - | - | text
A01.051 | 5 | 51 | 05 Static stress Maintenance | Reactive power voltage characteristic curve Q(U) unrestricted adjustable according to VDE-AR-N 4110/20/30? | Indicate yes if the reactive power voltage characteristic Q(U) is adjustable without restrictions according to VDE-AR-N 4110/20/30. If no, then indicate restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.052 | 6 | 52 | 05 Static stress Maintenance | Reactive power characteristic curve as a function of power Q(P) unrestricted adjustable according to VDE-AR-N 4110? | Indicate yes if the characteristic curve reactive power characteristic curve as a function of the active power Q(P) is adjustable without restrictions according to VDE-AR-N 4110. If no, then indicate restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.053 | 7 | 53 | 05 Static stress Maintenance | Reactive power characteristic with voltage limitating function unrestricted adjustable according to VDE-AR-N 4110/20/30? | Indicate yes if the reactive power with voltage limitation function is adjustable without restrictions according to VDE-AR-N 4110/20/30. If no, then indicate restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.054 | 8 | 54 | 05 Static stress Maintenance | Displacement factor cos(phi) unrestricted adjustable according to VDE-AR-N 4110/20/30? | Indicate yes if the displacement factor cos(phi) is adjustable without restrictions according to VDE-AR-N 4110/20/30. If no, then indicate restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.058 | 1 | 58 | 06 Dynamic grid support | Min. adjustable k-factor (only for type 2) | At generating unit min. practically adjustable, has to be tested in the model as well | Manufacturer | kmin | - | decimal number
A01.059 | 2 | 59 | 06 Dynamic grid support | Max. adjustable k-factor (only for type 2) | At generating unit max. practically adjustable, has to be tested in the model as well | Manufacturer | kmax | - | decimal number
A01.060 | 3 | 60 | 06 Dynamic grid support | Min. step size of the k-factor (only for type 2) | Specify min. adjustable step size of the k-factor (max. 0.5 ) | Manufacturer |  | - | decimal number
A01.061 | 4 | 61 | 06 Dynamic grid support | Is it possible to parameterise HVRT and LVRT thresholds independently of each other? (only for type 2) | Specify yes if HVRT and LVRT thresholds can be parameterised independently of each other. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.062 | 5 | 62 | 06 Dynamic grid support | Multiple faults can be driven through? | Yes, if the generating unit can pass multiple faults according to VDE-AR N 4110/20/30. | Unit certifier | - | - | logical value | Value1: Yes; Value2: No
A01.063 | 6 | 63 | 06 Dynamic grid support | Multiple errors possible again after 30 min? | Yes, if the generating unit can pass multiple faults according to VDE-AR N 4110/20/30 after 30 minutes. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.064 | 7 | 64 | 06 Dynamic grid support | Was a machine transformer present during the FRT measurement? (only for type 1) | Necessary for the evaluation of network oscillations | Measuring institute |  |  | logical value | Value1: Yes; Value2: No
A01.065 | 8 | 65 | 06 Dynamic grid support | Relative short-circuit voltage uk of the measured transformer (only for type 1) | In the case of type 1 generating units, indicate the relative short-circuit voltage uk of the machine transformer used in the FRT measurement (if present, see ID A01.064), necessary for the evaluation of mains oscillations. | Measuring institute | uk | % | decimal number
A02.001 |  |  | 06 Dynamic grid support | Implementation site of the HVRT and LVRT thresholds | HVRT and LVRT thresholds see ID A01.061, at PGU terminals or HV machine transformer (high voltage side). | Manufacturer |  | - | text | Value1: PGU terminals; Value2: HVRT generator transformer
A01.055 | 9 | 55 | 07 Control | Requirements for active power feed-in at overfrequency of the P(f) characteristic curve are fulfilled? | Indicate yes if requirements for active power feed-in at overfrequency of the P(f) characteristic are met. If no, then specify restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.056 | 10 | 56 | 07 Control | Requirements for active power feed-in at underfrequency of the P(f) characteristic curve are fulfilled? | Indicate yes if requirements for active power feed-in at underfrequency of the P(f) characteristic are met. If no, then specify restrictions. | Unit certifier | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.057 | 11 | 57 | 07 Control | Frequency-dependent mode for partial network operability possible? | To be designated according to VDE-AR-N 4110/20/30 Chapter 11.4.9 | Manufacturer | - | - | text | Value1: Yes; Value2: No; Value3: With restrictions: (fill in)
A01.066 | 1 | 66 | 07 Control | Min. setting time 3 τ for reactive power step (only relevant for VDE-AR-N 4110) | Specify min. adjustable time for the reactive power jump (cf. Fig. 7 in VDE-AR N 4110). | Manufacturer or unit certifier | 3 τ | s | decimal number
A01.067 | 2 | 67 | 07 Control | Max. settling time with min. setting time of 3 τ (only relevant for VDE-AR-N 4110) | Indicate max. measured settling time at min. setting time of 3 τ (see ID A01.066) for the reactive power step (cf. Fig. 7 in VDE-AR N 4110). | Manufacturer or unit certifier | Tein_Δx | s | decimal number
A01.068 | 3 | 68 | 07 Control | PT1 behaviour fulfilled in case of Q setpoint changes? (only relevant for VDE-AR-N 4110) | Specify yes if setpoint changes of the reactive power correspond to PT1 behaviour | Unit certifier | - | - | logical value | Value1: Yes; Value2: No
A01.069 | 4 | 69 | 07 Control | Max. active power control deviation | The reference value is the rated active power PrE (see ID A01.018). | Measuring institute |  | % PrE | decimal number
A01.070 | 5 | 70 | 07 Control | Reactive power behaviour is possible with the last received value in case of a communication failure between the generating unit and the PGS controller? | If there is no PGS controller, in the event of a failure of the communication between the generating unit and the telecontrol system | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.071 | 6 | 71 | 07 Control | Reactive power behaviour is possible with an adjustable reactive power value in case of a communication failure between the generating unit and the PGS controller? | If no PGS controller is available, in case of communication failure between the generating unit and the telecontrol system. Reactive power value adjustable in the range from max. underexcited to max. overexcited. If the reactive power value is fixed and cannot be changed, specify ''No'' and explain this restriction under ID A01.012. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.072 | 7 | 72 | 07 Control | Behaviour is possible with an adjustable cos(phi) in case of communication failure between the generating unit and the PGS controller? | If no PGS controller is available, in case of communication failure between the generating unit and the telecontrol system. cos(phi) adjustable in the range from max. underexcited to max. overexcited. If the reactive power value is fixed and cannot be changed, specify ''No'' and explain this restriction under ID A01.012. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.073 | 8 | 73 | 07 Control | In case of a communication failure between the generating unit and the PGS controller, is the switchover to another reactive power characteristic curve method possible? | If no PGS controller is available, in case of communication failure between the generating unit and the telecontrol system. Typical reactive power curve methods are Q(U), Q(P) and cos(phi). | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.074 | 9 | 74 | 07 Control | Active power behavior in case of communication failure between generation unit and PGS controller with last received value possible? (optional specification) | If there is no PGS controller, in the event of a failure of the communication between the generating unit and the telecontrol system | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.075 | 10 | 75 | 07 Control | Active power behavior in case of communication failure between generating unit and PGS controller with adjustable active power value possible? (optional specification) | If no PGS controller is available, in case of communication failure between the generating unit and the telecontrol system. Active power value adjustable in the range from 0 % PrE to 100 % PrE (see ID A01.018). | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A02.002 |  |  | 07 Control | Test for interception on own demand operation or fast resynchronization successfully passed? (only for VDE-AR-N 4120/30) | Has the test according to VDE-AR-N 4120/30 chapter 11.2.8.2 been passed successfully? | Manufacturer or Measuring institute |  | - | logical value | Value1: Yes; Value2: No
A02.003 | 4 | 69 | 07 Control | Max. Reactive power control deviation (optional specification) | The reference value is the rated active power PrE (see ID A01.018). | Measuring institute |  | % PrE | decimal number | bar: Value4 to Value5
A02.004 |  |  | 07 Control | Min. transient time for reactive power jump (only relevant for VDE-AR-N 4120) | Specify min. transient time for reactive power step (cf. Fig. C.2 in VDE-AR N 4120) | Manufacturer, Measuring institute or Unit certifier | Ton_90 % | s | decimal number | bar: Value4 to Value5
A01.076 | 1 | 76 | 08 Power Quality | Max. number of switching operations | Max. Max. number of switching operations of the generating unit within 120 min. Maximum value from all measurements of the switching operations according to FGW TR3: Connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, when switching between generator stages. | Measuring institute | N120 | - | integer
A01.077 | 2 | 77 | 08 Power Quality | Max. flicker form factor at connection and Ψk = 30°. | The max. flicker form factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 30° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | kf (Ψk = 30°) | - | decimal number
A01.078 | 3 | 78 | 08 Power Quality | Max. Flicker form factor at connection and Ψk = 50°. | The max. flicker form factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 50° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | kf (Ψk = 50°) | - | decimal number
A01.079 | 4 | 79 | 08 Power Quality | Max. Flicker shape factor at connection and Ψk = 70 | The max. flicker form factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 70° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | kf (Ψk = 70°) | - | decimal number
A01.080 | 5 | 80 | 08 Power Quality | Max. Flicker form factor at connection and Ψk = 85°. | The max. flicker form factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 85° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | kf (Ψk = 85°) | - | decimal number
A01.081 | 6 | 81 | 08 Power Quality | Max. voltage-effective switching factor at connection and Ψk = 30°. | The max. effective voltage switching factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, when switching between generator stages) at Ψk = 30° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | ku (Ψk = 30°) | - | decimal number
A01.082 | 7 | 82 | 08 Power Quality | Max. voltage-effective switching factor at connection and Ψk = 50°. | The max. effective voltage switching factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018 and, if applicable, switching between generator stages) at Ψk = 50° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | ku (Ψk = 50°) | - | decimal number
A01.083 | 8 | 83 | 08 Power Quality | Max. voltage-effective switching factor at connection and Ψk = 70°. | The maximum effective voltage switching factor from all measurements of the switching operations according to FGW TR3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 70° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | ku (Ψk = 70°) | - | decimal number
A01.084 | 9 | 84 | 08 Power Quality | Max. voltage-effective switching factor at connection and Ψk = 85°. | The max. effective voltage switching factor from all measurements of the switching operations according to FGW TG3 (connection at <0.1 PrE, connection at 1.0 PrE, disconnection at 1.0 PrE (see ID A01.018) and, if applicable, switching between generator stages) at Ψk = 85° shall be specified. The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | ku (Ψk = 85°) | - | decimal number
A01.085 | 10 | 85 | 08 Power Quality | Max. flicker coefficient at Ψk = 30° | The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | c (Ψk = 30°) | - | decimal number
A01.086 | 11 | 86 | 08 Power Quality | Max. flicker coefficient at Ψk = 50° | The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | c (Ψk = 50°) | - | decimal number
A01.087 | 12 | 87 | 08 Power Quality | Max. flicker coefficient at Ψk = 70° | The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | c (Ψk = 70°) | - | decimal number
A01.088 | 13 | 88 | 08 Power Quality | Max. flicker coefficient at Ψk = 85° | The reference value is the rated apparent power SrE (see ID A01.022) according to VDE-AR-N 4110/20/30. | Measuring institute | c (Ψk = 85°) | - | decimal number
A01.089 | 14 | 89 | 08 Power Quality | Max. quotient of the currents from negative and positive sequence | Specify the exact value of the asymmetries | Measuring institute | iunsymPGU | % | decimal number
A01.091 | 16 | 91 | 08 Power Quality | Justification for asymmetries (only for VDE-AR-N 4110/20) | If max. quotient of currents from counter and positive sequence system (see ID A01.089) > 1.5 % (VDE-AR-N 4110) or > 2.5 % (VDE-AR-N 4120) an explanation is necessary | Unit certifier | - | - | text
A01.092 | 1 | 92 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 2) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I2/In | % | decimal number
A01.093 | 2 | 93 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 3) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I3/In | % | decimal number
A01.094 | 3 | 94 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 4) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I4/In | % | decimal number
A01.095 | 4 | 95 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 5) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I5/In | % | decimal number
A01.096 | 5 | 96 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 6) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I6/In | % | decimal number
A01.097 | 6 | 97 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 7) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I7/In | % | decimal number
A01.098 | 7 | 98 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 8) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I8/In | % | decimal number
A01.099 | 8 | 99 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 9) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I9/In | % | decimal number
A01.100 | 9 | 100 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 10) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I10/In | % | decimal number
A01.101 | 10 | 101 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 11) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I11/In | % | decimal number
A01.102 | 11 | 102 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 12) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I12/In | % | decimal number
A01.103 | 12 | 103 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 13) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I13/In | % | decimal number
A01.104 | 13 | 104 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 14) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I14/In | % | decimal number
A01.105 | 14 | 105 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 15) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I15/In | % | decimal number
A01.106 | 15 | 106 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 16) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I16/In | % | decimal number
A01.107 | 16 | 107 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 17) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I17/In | % | decimal number
A01.108 | 17 | 108 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 18) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I18/In | % | decimal number
A01.109 | 18 | 109 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 19) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I19/In | % | decimal number
A01.110 | 19 | 110 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 20) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I20/In | % | decimal number
A01.111 | 20 | 111 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 21) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I21/In | % | decimal number
A01.112 | 21 | 112 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 22) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I22/In | % | decimal number
A01.113 | 22 | 113 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 23) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I23/In | % | decimal number
A01.114 | 23 | 114 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 24) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I24/In | % | decimal number
A01.115 | 24 | 115 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 25) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I25/In | % | decimal number
A01.116 | 25 | 116 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 26) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I26/In | % | decimal number
A01.117 | 26 | 117 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 27) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I27/In | % | decimal number
A01.118 | 27 | 118 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 28) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I28/In | % | decimal number
A01.119 | 28 | 119 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 29) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I29/In | % | decimal number
A01.120 | 29 | 120 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 30) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I30/In | % | decimal number
A01.121 | 30 | 121 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 31) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I31/In | % | decimal number
A01.122 | 31 | 122 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 32) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I32/In | % | decimal number
A01.123 | 32 | 123 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 33) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I33/In | % | decimal number
A01.124 | 33 | 124 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 34) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I34/In | % | decimal number
A01.125 | 34 | 125 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 35) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I35/In | % | decimal number
A01.126 | 35 | 126 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 36) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I36/In | % | decimal number
A01.127 | 36 | 127 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 37) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I37/In | % | decimal number
A01.128 | 37 | 128 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 38) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I38/In | % | decimal number
A01.129 | 38 | 129 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 39) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I39/In | % | decimal number
A01.130 | 39 | 130 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 40) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I40/In | % | decimal number
A01.131 | 40 | 131 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 41) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I41/In | % | decimal number
A01.132 | 41 | 132 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 42) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I42/In | % | decimal number
A01.133 | 42 | 133 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 43) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I43/In | % | decimal number
A01.134 | 43 | 134 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 44) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I44/In | % | decimal number
A01.135 | 44 | 135 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 45) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I45/In | % | decimal number
A01.136 | 45 | 136 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 46) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I46/In | % | decimal number
A01.137 | 46 | 137 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 47) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I47/In | % | decimal number
A01.138 | 47 | 138 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 48) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I48/In | % | decimal number
A01.139 | 48 | 139 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 49) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I49/In | % | decimal number
A01.140 | 49 | 140 | 09 harmonic currents: harmonic | Max. measured harmonic current (ordinal number: 50) | Quotient Iν/In in % with ν as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I50/In | % | decimal number
A01.141 | 1 | 141 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 1.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I1,5/In | % | decimal number
A01.142 | 2 | 142 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 2.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I2,5/In | % | decimal number
A01.143 | 3 | 143 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 3.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I3,5/In | % | decimal number
A01.144 | 4 | 144 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 4.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I4,5/In | % | decimal number
A01.145 | 5 | 145 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 5.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I5,5/In | % | decimal number
A01.146 | 6 | 146 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 6.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I6,5/In | % | decimal number
A01.147 | 7 | 147 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 7.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I7,5/In | % | decimal number
A01.148 | 8 | 148 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 8.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I8,5/In | % | decimal number
A01.149 | 9 | 149 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 9.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I9,5/In | % | decimal number
A01.150 | 10 | 150 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 10.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I10,5/In | % | decimal number
A01.151 | 11 | 151 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 11.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I11,5/In | % | decimal number
A01.152 | 12 | 152 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 12.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I12,5/In | % | decimal number
A01.153 | 13 | 153 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 13.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I13,5/In | % | decimal number
A01.154 | 14 | 154 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 14.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I14,5/In | % | decimal number
A01.155 | 15 | 155 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 15.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I15,5/In | % | decimal number
A01.156 | 16 | 156 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 16.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I16,5/In | % | decimal number
A01.157 | 17 | 157 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 17.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I17,5/In | % | decimal number
A01.158 | 18 | 158 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 18.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I18,5/In | % | decimal number
A01.159 | 19 | 159 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 19.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I19,5/In | % | decimal number
A01.160 | 20 | 160 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 20.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I20,5/In | % | decimal number
A01.161 | 21 | 161 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 21.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I21,5/In | % | decimal number
A01.162 | 22 | 162 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 22.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I22,5/In | % | decimal number
A01.163 | 23 | 163 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 23.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I23,5/In | % | decimal number
A01.164 | 24 | 164 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 24.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I24,5/In | % | decimal number
A01.165 | 25 | 165 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 25.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I25,5/In | % | decimal number
A01.166 | 26 | 166 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 26.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I26,5/In | % | decimal number
A01.167 | 27 | 167 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 27.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I27,5/In | % | decimal number
A01.168 | 28 | 168 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 28.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I28,5/In | % | decimal number
A01.169 | 29 | 169 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 29.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I29,5/In | % | decimal number
A01.170 | 30 | 170 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 30.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I30,5/In | % | decimal number
A01.171 | 31 | 171 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 31.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I31,5/In | % | decimal number
A01.172 | 32 | 172 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 32.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I32,5/In | % | decimal number
A01.173 | 33 | 173 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 33.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I33,5/In | % | decimal number
A01.174 | 34 | 174 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 34.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I34,5/In | % | decimal number
A01.175 | 35 | 175 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 35.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I35,5/In | % | decimal number
A01.176 | 36 | 176 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 36.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I36,5/In | % | decimal number
A01.177 | 37 | 177 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 37.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I37,5/In | % | decimal number
A01.178 | 38 | 178 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 38.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I38,5/In | % | decimal number
A01.179 | 39 | 179 | 10 harmonic currents: interharmonic | Max. measured interharmonic current (ordinal number: 39.5) | Quotient Iμ/In in % with μ as ordinal number and the reference value nominal current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I39,5/In | % | decimal number
A01.180 | 1 | 180 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 42; 2.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I42s/In | % | decimal number
A01.181 | 2 | 181 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 46; 2.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I46s/In | % | decimal number
A01.182 | 3 | 182 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 50; 2.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I50s/In | % | decimal number
A01.183 | 4 | 183 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 54; 2.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I54/In | % | decimal number
A01.184 | 5 | 184 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 58; 2.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I58/In | % | decimal number
A01.185 | 6 | 185 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 62; 3.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I62/In | % | decimal number
A01.186 | 7 | 186 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 66; 3.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I66/In | % | decimal number
A01.187 | 8 | 187 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 70; 3.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I70/In | % | decimal number
A01.188 | 9 | 188 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 74; 3.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I74/In | % | decimal number
A01.189 | 10 | 189 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 78; 3.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I78/In | % | decimal number
A01.190 | 11 | 190 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 82; 4.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I82/In | % | decimal number
A01.191 | 12 | 191 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 86; 4.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I86/In | % | decimal number
A01.192 | 13 | 192 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 90; 4.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I90/In | % | decimal number
A01.193 | 14 | 193 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 94; 4.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I94/In | % | decimal number
A01.194 | 15 | 194 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 98; 4.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I98/In | % | decimal number
A01.195 | 16 | 195 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 102; 5.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I102/In | % | decimal number
A01.196 | 17 | 196 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 106; 5.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I106/In | % | decimal number
A01.197 | 18 | 197 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 110; 5.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I110/In | % | decimal number
A01.198 | 19 | 198 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 114; 5.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I114/In | % | decimal number
A01.199 | 20 | 199 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 118; 5.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I118/In | % | decimal number
A01.200 | 21 | 200 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 122; 6.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I122/In | % | decimal number
A01.201 | 22 | 201 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 126; 6.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I126/In | % | decimal number
A01.202 | 23 | 202 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 130; 6.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I130/In | % | decimal number
A01.203 | 24 | 203 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 134; 6.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I134/In | % | decimal number
A01.204 | 25 | 204 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 138; 6.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I138/In | % | decimal number
A01.205 | 26 | 205 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 142; 7.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I142/In | % | decimal number
A01.206 | 27 | 206 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 146; 7.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I146/In | % | decimal number
A01.207 | 28 | 207 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 150; 7.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I150/In | % | decimal number
A01.208 | 29 | 208 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 154; 7.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I154/In | % | decimal number
A01.209 | 30 | 209 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 158; 7.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I158/In | % | decimal number
A01.210 | 31 | 210 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 162; 8.1 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I162/In | % | decimal number
A01.211 | 32 | 211 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 166; 8.3 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I166/In | % | decimal number
A01.212 | 33 | 212 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 170; 8.5 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I170/In | % | decimal number
A01.213 | 34 | 213 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 174; 8.7 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I174/In | % | decimal number
A01.214 | 35 | 214 | 11 harmonic currents: higher frequency | Max. measured supraharmonic current (ordinal number: 178; 8.9 kHz) | Ratio Ih/In in % with h as ordinal number and the reference value rated current In (see ID A01.016) as well as rated voltage UrE (see ID A01.015) | Measuring institute | I178/In | % | decimal number
A01.215 | 1 | 215 | 12 Uncoupling protection | Is the protection device installed in the generating unit and included in the scope of certification? | Indicate yes if the protection device is installed in the generating unit and included in the scope of certification | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.216 | 2 | 216 | 12 Uncoupling protection | Protection device works independently of control functions? | Yes, if in the case of an integrated protective function, this is designed to be independent of the control function (compare VDE-AR N 4110 Chapter 11.2.10). | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.217 | 3 | 217 | 12 Uncoupling protection | Test terminal strip present? | Protection test possible without disconnection of wires? | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.218 | 4 | 218 | 12 Uncoupling protection | Evaluation of the voltage for the protection device | Voltage that is evaluated by the PGU (Power generating Unit) (for IT network conductor-conductor, otherwise conductor-earth). | Manufacturer | - | - | text | Value1: phase-to-ground; Value2: phase-to-phase
A01.219 | 5 | 219 | 12 Uncoupling protection | Intrinsic time of the protection device (if protection device is in the scope of certification) | Specify the intrinsic time of the protection device if it was included in the scope of certification. | Manufacturer or Measuring institute | - | ms | integer
A01.220 | 6 | 220 | 12 Uncoupling protection | UPS for 5 s bridging time installed? | Yes, if UPS for 5 s bridging time is installed and included in the scope of certification (compare VDE-AR N 4110/20/30 chapter 11.2.10). | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.221 | 7 | 221 | 12 Uncoupling protection | Is the coupling switch installed in the generating unit and included in the scope of certification? | Indicate yes if the coupling switch is installed as standard in the generating unit, is included in the scope of certification and is designed for the continuous and short-circuit currents of the generating unit. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.222 | 8 | 222 | 12 Uncoupling protection | Shutdown of the coupling switch in case of failure of the auxiliary power supply? | e.g. in the event of a UPS (Uninterruptible Power Supply) failure | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.223 | 9 | 223 | 12 Uncoupling protection | Intrinsic time of the coupling switch (if coupling switch is in the scope of certification) | Specify the intrinsic time of the coupling switch if it was included in the scope of certification. | Manufacturer or Measuring institute | - | ms | integer
A01.224 | 10 | 224 | 12 Uncoupling protection | Testing of the entire functional chain (if protective device and coupling switch are included in the scope of certification) | Overall functional chain: Functional test consisting of excitation and triggering of the protective device as well as the coupling switch, failure of the auxiliary power supply (signal + triggering of the coupling switch), failure of the measuring voltage, if applicable feedback from the coupling switch if necessary. | Manufacturer or Measuring institute | - | - | logical value | Value1: Yes; Value2: No
A01.225 | 11 | 225 | 12 Uncoupling protection | Number of adjustable levels for undervoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | - | integer
A01.226 | 12 | 226 | 12 Uncoupling protection | Min. adjustable voltage threshold for undervoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | V | decimal number
A01.227 | 13 | 227 | 12 Uncoupling protection | Max. adjustable time threshold for undervoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | s | decimal number
A01.228 | 14 | 228 | 12 Uncoupling protection | Number of adjustable levels for overvoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | - | integer
A01.229 | 15 | 229 | 12 Uncoupling protection | Max. adjustable voltage threshold for overvoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | V | decimal number
A01.230 | 16 | 230 | 12 Uncoupling protection | Max. adjustable time threshold for overvoltage protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | s | decimal number
A01.231 | 17 | 231 | 12 Uncoupling protection | Number of adjustable levels for frequency drop protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | - | integer
A01.232 | 18 | 232 | 12 Uncoupling protection | Min. adjustable frequency threshold for frequency drop protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | Hz | decimal number
A01.233 | 19 | 233 | 12 Uncoupling protection | Max. adjustable time threshold for frequency drop protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | s | decimal number
A01.234 | 20 | 234 | 12 Uncoupling protection | Number of adjustable levels for frequency increase protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | - | integer
A01.235 | 21 | 235 | 12 Uncoupling protection | Max. adjustable frequency threshold for frequency increase protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | Hz | decimal number
A01.236 | 22 | 236 | 12 Uncoupling protection | Max. adjustable time threshold for frequency increase protection | Decoupling protection for compliance with grid operator specifications | Manufacturer |  | s | decimal number
A01.237 | 23 | 237 | 12 Uncoupling protection | Is an automatic reconnection of the generating unit possible after protection triggering? | Indicate yes if the generating unit can be automatically reconnected after protection triggering. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.238 | 24 | 238 | 12 Uncoupling protection | Are the switch-on thresholds after protection triggering parameterisable? | Compare VDE-AR-N 4110/20/30 Chapter 10.4.2 | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.239 | 25 | 239 | 12 Uncoupling protection | Can the connection thresholds be parameterised independently of each other in undisturbed mains operation and after protection triggering? | Indicate yes if the connection thresholds can be parameterised independently of each other in undisturbed mains operation and after protective triggering. | Manufacturer | - | - | logical value | Value1: Yes; Value2: No
A01.240 | 1 | 240 | 13 Short circuit current contribution | Initial short-circuit alternating current | Root Mean Square (RMS) value of the AC component at short-circuit occurrence, max. value from all measurements | Measuring institute | Ik" | kA | decimal number
A01.241 | 2 | 241 | 13 Short circuit current contribution | Peak short-circuit current | Max. Instantaneous value of the short-circuit current, max. value from all measurements | Measuring institute | ip | kA | decimal number
A01.242 | 3 | 242 | 13 Short circuit current contribution | Continuous short-circuit alternating current | Root Mean Square (RMS) value of the short-circuit current after all equalisation processes have decayed, max. value from all measurements | Measuring institute | Ik | kA | decimal number
A01.243 | 4 | 243 | 13 Short circuit current contribution | Rated voltage of the generator (only for type 1) | Short-circuit current calculation according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) | Manufacturer | UrG | V | decimal number
A01.244 | 5 | 244 | 13 Short circuit current contribution | Resistance of the generator (only for type 1) | Short-circuit current calculation according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) | Manufacturer | RG | Ohm | decimal number
A01.245 | 6 | 245 | 13 Short circuit current contribution | Related saturated subtransient reactance of the longitudinal axis (only for type 1) | Short-circuit current calculation according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) | Manufacturer | xd'' | Ohm | decimal number
A01.246 | 7 | 246 | 13 Short circuit current contribution | Related saturated subtransient reactance of the transverse axis (only for type 1) | Short-circuit current calculation according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) | Manufacturer | xq'' | Ohm | decimal number
A01.247 | 8 | 247 | 13 Short circuit current contribution | Displacement factor in rated operation (only for type 1) | Short-circuit current calculation according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) | Manufacturer | cos(φrG) | - | decimal number
A01.248 | 9 | 248 | 13 Short circuit current contribution | RMS (root mean square) value of the source current for single-pole faults (only for type 2 full inverters) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | I(1)sk1PF | A | decimal number
A01.249 | 10 | 249 | 13 Short circuit current contribution | RMS value of the source current for two-pole faults (only for type 2 full inverters) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | I(1)sk2PF | A | decimal number
A01.250 | 11 | 250 | 13 Short circuit current contribution | RMS value of the source current for three-pole faults (only for type 2 full inverters) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | IskPF | A | decimal number
A01.251 | 12 | 251 | 13 Short circuit current contribution | Short-circuit counter impedance only for integer k-factors (only for type 2 full inverters) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | Z(2)PF | Ohm | decimal number
A01.252 | 13 | 252 | 13 Short circuit current contribution | Factor for calculating the surge short-circuit current referred to the top voltage side (only for type 2 with double-fed asynchronous machine) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | KWD | - | decimal number
A01.253 | 14 | 253 | 13 Short circuit current contribution | Highest instantaneous value of the short-circuit current with three-pole short-circuit (only for type 2 with double-fed asynchronous machine) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | iWDmax | A | decimal number
A01.254 | 15 | 254 | 13 Short circuit current contribution | Rated voltage of the block transformer on the high voltage side (only for type 2 with double-fed asynchronous machine) |  | Manufacturer | UrTHV | V | decimal number
A01.255 | 16 | 255 | 13 Short circuit current contribution | Rated transformation ratio of the block transformer (only for type 2 asynchronous machine) | Specify direct transformation ratio (e.g. 50 instead of 20kV/0.4kV). To be shown according to Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | tr | - | decimal number
A01.256 | 17 | 256 | 13 Short circuit current contribution | Impedance of the block transformer on the high voltage side (only for type 2 asynchronous machine) | Impedance of the block transformer of the high voltage side (only for type 2 asynchronous machine). To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | ZTHV | Ohm | decimal number
A01.257 | 18 | 257 | 13 Short circuit current contribution | Impedance of the asynchronous generator (only for type 2 asynchronous machine) | To be shown in accordance with Table 15 (VDE-AR-N 4110), Table 12 (VDE-AR-N 4120) or Table 9 (VDE-AR-N 4130) for the calculation of the short-circuit alternating currents according to DIN EN 60909-0. | Manufacturer | ZG | Ohm | decimal number
A01.258 | 1 | 258 | 14 Self-protection | Undervoltage protection U< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.259 | 2 | 259 | 14 Self-protection | Triggering time undervoltage protection tU< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.260 | 3 | 260 | 14 Self-protection | Undervoltage protection U<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.261 | 4 | 261 | 14 Self-protection | Triggering time undervoltage protection tU<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.262 | 5 | 262 | 14 Self-protection | Undervoltage protection U<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.263 | 6 | 263 | 14 Self-protection | Triggering time undervoltage protection tU<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.264 | 7 | 264 | 14 Self-protection | Undervoltage protection U<<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.265 | 8 | 265 | 14 Self-protection | Triggering time undervoltage protection tU<<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.266 | 9 | 266 | 14 Self-protection | Undervoltage protection U<<<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.267 | 10 | 267 | 14 Self-protection | Triggering time undervoltage protection tU<<<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.268 | 11 | 268 | 14 Self-protection | Overvoltage protection U> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.269 | 12 | 269 | 14 Self-protection | Triggering time overvoltage protection tU> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.270 | 13 | 270 | 14 Self-protection | Overvoltage protection U>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.271 | 14 | 271 | 14 Self-protection | Triggering time overvoltage protection tU>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.272 | 15 | 272 | 14 Self-protection | Overvoltage protection U>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.273 | 16 | 273 | 14 Self-protection | Triggering time overvoltage protection tU>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.274 | 17 | 274 | 14 Self-protection | Overvoltage protection U>>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.275 | 18 | 275 | 14 Self-protection | Triggering time overvoltage protection tU>>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.276 | 19 | 276 | 14 Self-protection | Overvoltage protection U>>>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | V | decimal number
A01.277 | 20 | 277 | 14 Self-protection | Triggering time overvoltage protection tU>>>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.278 | 21 | 278 | 14 Self-protection | Underfrequency protection f< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.279 | 22 | 279 | 14 Self-protection | Triggering time underfrequency protection tf< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.280 | 23 | 280 | 14 Self-protection | Underfrequency protection f<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.281 | 24 | 281 | 14 Self-protection | Triggering time underfrequency protection tf<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.282 | 25 | 282 | 14 Self-protection | Underfrequency protection f<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.283 | 26 | 283 | 14 Self-protection | Triggering time underfrequency protection tf<<< (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.284 | 27 | 284 | 14 Self-protection | Overfrequency protection f> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.285 | 28 | 285 | 14 Self-protection | Triggering time overfrequency protection tf> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.286 | 29 | 286 | 14 Self-protection | Overfrequency protection f>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.287 | 30 | 287 | 14 Self-protection | Triggering time overfrequency protection tf>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.288 | 31 | 288 | 14 Self-protection | Overfrequency protection f>>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | Hz | decimal number
A01.289 | 32 | 289 | 14 Self-protection | Triggering time overfrequency protection tf>> (self-protection) | Intrinsic protection values of the generating unit according to manufacturer's specifications | Manufacturer |  | s | decimal number
A01.290 | 33 | 290 | 14 Self-protection | Overcurrent protection I> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | A | decimal number
A01.291 | 34 | 291 | 14 Self-protection | Triggering time overcurrent protection tI> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | s | decimal number
A01.292 | 35 | 292 | 14 Self-protection | Overcurrent protection I>> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | A | decimal number
A01.293 | 36 | 293 | 14 Self-protection | Triggering time overcurrent protection tI>> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | s | decimal number
A01.294 | 37 | 294 | 14 Self-protection | Overcurrent protection I>>> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | A | decimal number
A01.295 | 38 | 295 | 14 Self-protection | Triggering time overcurrent protection tI>>> (self-protection) | Intrinsic protection values of the generating unit according to the manufacturer's specifications; if non-linear protection characteristics are used (e.g. fuses), these must be specified separately in ID A02.005. | Manufacturer |  | s | decimal number
A02.005 |  |  | 14 Self-protection | Explanations for self-protection (optional specification) | Explanation of self-protection when using non-linear protection characteristics, etc. | Manufacturer |  |  | text

## Hints
Theme | Explanation
General | This template is intended to accelerate and standardise the certification process and to facilitate the exchange of data. This digital annex to the unit certificate is a summary of the most important electrical parameters and properties of the generating units contained in the unit certificate and is to be issued by the accredited certification body for equipment. This is to ensure that all equipment certifiers have to report the characteristics and properties required according to VDE-AR-N 4110/20/30 and FGW TR 8 completely and uniformly. For the equipment certifier, this makes it much easier to find the necessary data more quickly and to avoid errors in the transmission of data.
Version number of the template | Any adjustments to the template are made directly through the sub-working group "Digitaler Anhang" of the meeting of the certification bodies. Modifications to the template will be published on the FGW website, additionally the meeting of the certification bodies of the FGW will be informed.
ID | Each attribute has a unique ID which only appears once and which will not change in later versions for existing attributes. This enables a unique assignment of the attributes both on the side of the user who fills in the data and on the side of the user who reads it out. In addition, the ID is used to establish references between the attributes. If new attributes are introduced in new versions of the table, they will also receive a new, previously unused ID. If an attribute changes significantly, a new ID is assigned to the changed attribute. The ID in the form AXX.YYY is composed as follows: A -> designation for the (digital) attachment XX -> version number in which the attribute was created or substantially changed YYY -> consecutive number in the respective version
Category | Serves the thematic classification and sorting of the attributes.
Attribute name | Compared to the attribute number, the attribute name may change over time.
Explanations of data input | Where necessary, there is an explanation for each attribute. Among other things, background information and the reason why the attribute is required are given.
To be filled out by | This column states who is responsible for obtaining the required information or where this information usually comes from. The unit certifier decides about the final entry.
Formula symbol | If applicable, there is a formula symbol for each attribute, which is based on the VDE-AR-N 4110/20/30, the FGW and other guidelines.
Unit | Only the specified base units are to be used for the electrical parameters, a conversion may be necessary.
Data type | The data type specifies the form in which the inputs are to be entered and processed. Here, a distinction is usually made between number, truth value (yes or no) and text.
PGU 1 … | From here on, the necessary information for the generating unit is entered. Each type of generating unit, which is evaluated in the unit certificate, must be entered in a column. If the columns are not sufficient, they can be extended to the right. If there are different electrical characteristics of the same type of generating unit (e.g. different voltage levels), these must be entered separately in columns. Electrical characteristics shall be entered without a unit. Only a comma is to be used as decimal separator. Separators for thousands are not permitted. Attributes with truth value are to be filled in exclusively with the corresponding drop-down selection options, they may not be left blank.
Creator of the template
The following people played a key role in the creation of this template:
Simon Borsutzki | FGW e.V. – Fördergesellschaft Windenergie und andere Dezentrale Energien
Dr. Michael Pufke | P&M Power Certification GmbH
Hannes Pietsch Oliver Berthold-Rehm | DNV Renewables Certification GmbH
Andreas Kollbach | Moeller Operating Engineering GmbH
Version (version date) | Version changes
01 (20.02.2023) | Initial creation/publication of the template
02 (27.09.2023) | 5 new attributes were added (A02.001 - A02.005), references were corrected, typos were corrected, explanations were clarified. Attributes A01.047 - A01.050 were assigned to category 02 Generation unit. Attributes A01.055, A01.056 and A01.057 were assigned to category 07 Control. Column G "To be filled in by" renamed to "Data source". Attribute A01.090 "Max. quotient of currents from negative and positive sequence < 1.5 %" deleted.